Feed water System Sample Specifications (30-2000 Gallon)

1.0	Furnish an open vented boiler feed water system, Hurst “Feedmiser,” model FM-     -     -     .  The system shall be a factory-packaged unit with pumps and trim factory piped and wired as specified herein.

2.0	The boiler feed tanks shall be constructed of (3/16” through 350 gallon, ¼” 400 gallon and >) carbon steel.  The tank opening shall include as a minimum a 3,000 lb. coupling for:  pump section connection, condensate return, drain, tank overflow, and two for vents to atmosphere.  The boiler feed system shall be supported with a structural steel support legs with a minimum height as required for the NPSHR of the pumps selected.  Provide for a steel base for pump supports.

3.0      A.	Automatic float type water level control for maintaining water level with                                              makeup-water.

B.	Water gauge glass set with bronze shut-off cocks and drain.

C.	Tank drain valve.

D.	Tank Thermometer

Optional Trim:

- Sacrificial magnesium anode.

- High temperature condensate return diffuser pipe, installed below the normal water level.

- Steam pre-heater assembly including a seam inlet strainer, a steam pressure reducing valve to reduce the steam inlet to 10 psi, and a self contained temperature regulator with a steam sparge tube to maintain the water at 180 degrees F.

4.0	Provide (simplex, duplex, triplex) boiler feed pump(s) of the centrifugal type.  Each pump shall be rated at       gpm with a discharge pressure of       psig.  Electrical supply shall be      /60/     , 3450 rpm, (ODP or TEFC).  Pumps seals shall be rated for 250 degrees.  Provide individual pump suction piping including a strainer with removable and cleanable basket, and gate type shut off valve.  Pumps shall operate as on/off and controlled by the respective boiler’s water level controls.  (Pumps shall be continuous run type to maintain boiler’s water level control automatically through the boiler’s proportioning water level control.  Provide for pump discharge orifice for field installation of a recirculation line for minimum pump flow).

Optional:  Provide pump discharge check valve and pressure gauge.

- Provide a factory wired NEMA 1 control panel enclosure including Allen-Bradley pump motor starters and heater, circuit breakers, pump selector and switches, and control panel lights for annunciation of pump operation.

Optional:  Provide for high and low water level controls, red lights, for annunciation, and alarm bell with silencer.  Provide dry contacts for activation of a chemical feed pump when the pump runs.

- Contractor shall install the feed water system as indicated on the project drawings.

Hurst Boiler & Welding Co., Inc.  www.hurstboiler.com